## Read Me
How to use Velocity MMP Loop Calculator
Step 1. Go to Sec 1 - "Configure Panel" Tab.
| On this tab, any space where info can be added is highlighted in |  |  |  | Amber
Step 2. | *Select the panel size from the drop down list
Step 3. | *Select the type(s) of Panel Module(s) required to fit in each port -
| *Note: | Once you have selected the required control panel, the number of available ports will be indicated
in the first coloumn, simply click on the module selection cells and select the required modules
from the drop down list
| *Note: | If you have selected an invalid quantity of modules, the modules fitted table will show an error
Step 4. | *Entering Sounders / Strobes - Current draw
| *Note: | If you have selected any VL-NCA or VL-NCB panel modules, you will be prompted to calculate
and fill in the amount of current draw required for each loop or circuit
Example: 1 x NAC Loop ( You require 2x sounder/strobes with 75 candela output -
each device will pull 185mA of current in alarm).
|  |  | Sum: | 185mA x 2 = 370mA | Enter: | 370
|  | *Note: | If the load is too high, or if you enter a load for the wrong circuit an error will be shown
Step 5. | *Enter the required System "Backup" time in hours
Step 6. | *Enter the required "Alarm Time" (example - 30 mins will be 0.5 hrs)
| *Note: | If you have selected an invalid quantity of modules, the modules fitted table will show an error
When all has been entered, move to Sec 2 - Addressable loop Calc tab to enter the panels loop contents.
Tab "Sec 2 - Addressable Loop Calc"
Step 7. Go to Sec 1 - "Configure Panel" Tab. | Section 1 | *Auxilary Power - If additional power is required via NAC module or Terminals A & B
|  |  |  | then manually enter in mA | mA
Step 8. Go to Sec 1 - "Configure Panel" Tab. | Section 2 | *Cable Characteristics - Enter from the drop downs the required fire cable thickness peer loop
Step 9. Go to Sec 1 - "Configure Panel" Tab. | Section 3 | *Loop Devices - Manually enter the required device totals per loop
|  | Note: | An Error message will appear in the loop totals if the number of devices has exceeded the
maximum for that specific loop
| Section 4 | No Action Required
Step 10. Go to Sec 1 - "Configure Panel" Tab. | Section 5 | Site Details - Optional **Enter (if required) the site details, project reference etc.
You are now ready to view / print the report
Tab "Sec 3 - Report"
Check that the report has the correct information.
Print
Close

## Sec 1 - Configure Panel
[29 empty] | Part Number | Description | L1 | L12 | L2 | L3 | L4 | L5 | L52 | L53 | L54 | L6 | L7 | L8 | L9 | L10 | L11 | L122 | IMAX | C1 | C2 | Alarm_LEDs | SND | AUX
[29 empty] | VL-MMP 6/0 | MMP 6 no Zone LED | 254 |  | 254 | 254 | 254 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 113 | 125 | 8 | 1000 | 1000
[29 empty] | VL-MMP 10/64 | MMP 10 and 64 Zone LED | 254 |  | 254 | 254 | 254 | 254 |  |  |  | 254 | 254 | 254 | 0 | 0 | 0 | 0 | 450 | 113 | 125 | 8 | 1000 | 1000
[29 empty] | VL-MMP 10/P/64 | MMP 10 with 64 Zone LED & Printer | 254 |  | 254 | 254 | 254 | 254 |  |  |  | 254 | 254 | 254 | 0 | 0 | 0 | 0 | 450 | 113 | 125 | 8 | 1000 | 1000
1: Select Control Panel |  | Actions Required in this Section > | * Control Panels Analogue Addressable: Select the required Control Panel from drop down list and then select the required Internal Panel modules | [25 empty] | VL-MMP 26/64 | MMP 26 with 64 LED | 254 |  | 254 | 254 | 254 | 254 |  |  |  | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 450 | 113 | 125 | 8 | 1000 | 1000
|  |  | * Sounder Load Amount - Add the current draw in mA expected from the Conventional sounder Circuits and the Auxilary 24V DC power. | [25 empty] | VL-MMP 26/P/64 | MMP 26 with 64 LED & Printer | 254 |  | 254 | 254 | 254 | 254 |  |  |  | 254 | 254 | 254 | 254 | 254 | 254 | 254 | 450 | 113 | 125 | 8 | 1000 | 1000
* Backup Battery Requirement & Alarm Time: Input the number of hours backup & the alarm time required
* Control Panels: Analogue Addressable |  |  | Max Addresses on each Loop | [11 empty] | Panel Current |  | Quiescent Current |  |  |  | Alarm Current
| Select Control Panel (below) |  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12 | Quiescent | Alarm | Total for selected Control Panel |  |  |  | Total for selected Control Panel
| Part Number | Description | [12 empty] | IQ(mA) | IA (mA)
* | VL-MMP 6/0 | MMP 6 no Zone LED | 254 | 254 | 254 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 125 | 113 |  |  |  | 125 |  |  | 254 | VL-MMP 6/0 | MMP 6 no Zone LED
| Number of Ports: | 6 | Max Addresses on each Loop Loop 1: Max Recommended Loops:; Max Addresses on each Loop Loop 7: 4
*Internal Panel Modules (Enter Below) |  |  | Max Addresses on each Loop Loop 3: *Sounders / Strobes (Enter Loads When Requested Below) | Summary of Fitted Modules (Review the selected Modules) |  |  |  | * System Backup & Alarm Time (Enter the required backup and Alarm Times)
Port No | * Module (Select) | Description | Max Addresses on each Loop Loop 1: IQ; Max Addresses on each Loop Loop 2: IAlm
Port 1 | None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [14 empty] | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7
Port 2 | None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | Module | Quantity |  | Input Standby Time Requirement | [9 empty] | Module | Description | IQ | IALM | Max_6 | Max_10 | Max_26
Port 3 | None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-SLC | 0 |  |  | * | 24 | hr(s) | [6 empty] | None | No Module Fitted | 0 | 0
Port 4 | None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-NCB | 0 | [11 empty] | VL-SLC | Velocity MMP - Loop Card Module | 58.1 | 58.1 | 2 | 4 | 8
Port 5 | None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-ZMB | 0 | [11 empty] | VL-NCB | Velocity MMP - Alarm Circuit Module | 23.3 | 54.3 | 6 | 10 | 26
Port 6 | None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-MIM | 0 | [11 empty] | VL-ZMB | Velocity MMP - Zone Monitor Module | 51.2 | 51.2 | 6 | 10 | 26
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-MRM | 0 |  | Alarm Time Requirement | [9 empty] | VL-MIM | Velocity MMP - Multi-Input Module | 48.6 | 48.6 | 6 | 10 | 26
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-NWM | 0 |  |  |  | 0.5 | hr(s) | [6 empty] | VL-MRM | Velocity MMP - Relay Module | 17.2 | 79.8 | 6 | 10 | 26
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-232 | 0 | [11 empty] | VL-NWM | Velocity MMP - Network Module | 28.7 | 28.7 | 1 | 1 | 1
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 |  | VL-LAN | 0 | [11 empty] | VL-232 | Velocity MMP - Printer Module | 41.2 | 41.2 | 1 | 1 | 1
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [14 empty] | VL-LAN | Velocity MMP - Ethernet Module | 46.5 | 46.5 | 1 | 1 | 1
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | Module Total |  | 0 | [11 empty] | VL-ZMA | Velocity MMP - Zone Monitor Module Class A | 19.7 | 51.2 | 6 | 10 | 26
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [14 empty] | VL-NCA | Velocity MMP - Alarm Circuit Module | 17.7 | 54.3 | 6 | 10 | 26
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [13 empty] | MODULE Lookup Table |  |  | Module Count | [15 empty] | Summary of fitted modules
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [13 empty] | Module |  |  | Installed Modules |  | VL-SLC | VL-NCB | VL-ZMB | VL-MIM | VL-MRM | VL-NWM | VL-232 | VL-LAN | VL-ZMA | VL-NCA |  |  |  |  | Module | Quantity
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [12 empty] | Port 1 | None |  | 1 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-SLC | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [13 empty] | Module |  | 2 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-NCB | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [12 empty] | Port 2 | None |  | 3 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-ZMB | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [13 empty] | module |  | 4 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-MIM | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [12 empty] | Port 3 | None |  | 5 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-MRM | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [13 empty] | module |  | 6 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-NWM | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [12 empty] | Port 4 | None |  | 7 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-232 | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [13 empty] | Module |  | 8 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-LAN | 0
| None | No Module Fitted | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0 | [12 empty] | Port 5 | None |  | 9 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-ZMA | 0
[28 empty] | Module |  | 10 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | VL-NCA | 0
TOTAL | Panel Module Load | Total Module Current | Max Addresses on each Loop Loop 1: 0; Max Addresses on each Loop Loop 2: 0; Max Addresses on each Loop Loop 3: Sounder Current; Max Addresses on each Loop Loop 8: 0; Max Addresses on each Loop Loop 10: mA | Fitted Panel Modules |  |  | 0 | Standby Backup |  |  | 24 | Hrs |  |  |  | Port 6 | None |  | 11 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | total | 0
|  | Total Current | Max Addresses on each Loop Loop 1: 113; Max Addresses on each Loop Loop 2: 125; Max Addresses on each Loop Loop 3: Load |  |  |  |  | Alarm Time |  |  | 0.5 | Hrs |  |  |  |  | Module |  | 12 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 7 | None |  | 13 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 14 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 8 | None |  | 15 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 16 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 9 | None |  | 17 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 18 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 10 | None |  | 19 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 20 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 11 | None |  | 21 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 22 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 12 | None |  | 23 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 24 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 13 | None |  | 25 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | Module |  | 26 | None |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 14 | None
[28 empty] | Module |  |  | totals |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | Port 15 | None
Module
[27 empty] | Port 16 | None
Module
[27 empty] | Port 17 | None
Module
[27 empty] | Port 18 | None
Module
[27 empty] | Port 19 | None
Module
[27 empty] | Port 20 | None
Module
[27 empty] | Port 21 | None
Module
[27 empty] | Port 22 | None
Module
[27 empty] | Port 23 | None
Module
[27 empty] | Port 24 | None
Module
[27 empty] | Port 25 | None
Module
[27 empty] | Port 26 | None
Addressable Systems Loop Calculation Spreadsheet

## Sec 2 - Addressable Loop Calc
[5 empty] | Addressable Loop Calculator v2 | [24 empty] | Part Number | Description | L1 | L12 | L2 | L3 | L4 | L5 | L52 | L53 | L54 | L6 | L7 | L8 | L9 | L10 | L11 | L122 | Column5 | Column6 | IMAX | C1 | C2 | Alarm_LEDs | SND | AUX
[30 empty] | VL-MMP 6/0 | MMP 6 no Zone LED | 254 |  | 254 | 254 | 254 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 450 | 113 | 125 | 8 | 1000 | 1000
[30 empty] | VL-MMP 10/64 | MMP 10 and 64 Zone LED | 254 |  | 254 | 254 | 254 | 254 | 254 |  |  | 254 | 254 | 254 | 0 | 0 | 0 | 0 |  |  | 450 | 113 | 125 | 8 | 1000 | 1000
1: Selected Control Panel | [29 empty] | VL-MMP 10/P/64 | MMP 10 with 64 Zone LED & Printer | 254 |  | 254 | 254 | 254 | 254 |  |  |  | 254 | 254 | 254 | 0 | 0 | 0 | 0 |  |  | 450 | 113 | 125 | 8 | 1000 | 1000
|  |  | Actions required in this section > |  |  |  |  | *Auxilary Power - If additional power is required via NAC module or Terminals A & B enter in | [11 empty] | mA | [9 empty] | VL-MMP 26/64 | MMP 26 with 64 LED | 254 |  | 254 | 254 | 254 | 254 | 254 |  |  | 254 | 254 | 254 | 254 | 254 | 254 | 254 |  |  | 450 | 113 | 125 | 8 | 1000 | 1000
[30 empty] | VL-MMP 26/P/64 | MMP 26 with 64 LED & Printer | 254 |  | 254 | 254 | 254 | 254 | 254 |  |  | 254 | 254 | 254 | 254 | 254 | 254 | 254 |  |  | 450 | 113 | 125 | 8 | 1000 | 1000
Control Panels: Analogue Addressable |  | Max Addresses on each Loop | [11 empty] | Total Panel Current |  | Quiescent Current |  |  |  |  | Alarm Current
|  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12 | Quiescent | Alarm | Total for selected Control Panel |  |  |  |  | Total for selected Control Panel
Part Number | Description | [12 empty] | IQ(mA) | IA (mA)
VL-MMP 6/0 | MMP 6 no Zone LED | 254 | 254 | 254 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 125 |  |  |  | 113 |  |  |  |  | 125 |  | 254 | VL-MMP 6/0 | MMP 6 no Zone LED
Auxillary Power Option
Total Aux Power drawn through VL-NCA or VL-NCB |  | Max Addresses on each Loop Loop 4: MAX:; Max Addresses on each Loop Loop 5: 1000; Max Addresses on each Loop Loop 6: (1000mA Per Module) | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0
Total Aux Power drawn through Power Supply Outputs Terminals x2 |  | Max Addresses on each Loop Loop 4: MAX:; Max Addresses on each Loop Loop 5: 2000; Max Addresses on each Loop Loop 6: (1000 mA per output) | 0 | 0 |  |  |  |  | 0 |  |  |  |  | 0
| This System >>>> | [18 empty] | 113 |  |  |  |  | 125
2: Select Cable Characteristics
Actions required in this section > |  | Max Addresses on each Loop Loop 4: *Cable Characteristics - Enter from the drop downs the required fire cable thickness peer loop
Cable Data |  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12 |  |  |  | Max Loop Current for Selected Cables
IM(mA)
Cable Thickness (mm) |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  |  | 450.4976 |  | Loop 1 Maximum |  |  |  | 450
Cable run length (m) |  | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 |  |  | 450.4976 |  | Loop 2 Maximum |  |  |  | 450
[16 empty] | 450.4976 |  | Loop 3 Maximum |  |  |  | 450
[16 empty] | 450.4976 |  | Loop 4 Maximum |  |  |  | 450
[16 empty] | 450.4976 |  | Loop 5 Maximum |  |  |  | 450
[16 empty] | 450.4976 |  | Loop 6 Maximum |  |  |  | 450 | [7 empty] | Allowabl cable sizes
[16 empty] | 450.4976 |  | Loop 7 Maximum |  |  |  | 450 | [7 empty] | 1
|  | Loop 1: 1; Loop 2: 1.5; Loop 3: 2.5 |  |  | 450.4976 |  | Loop 8 Maximum |  |  |  | 450 | [7 empty] | 1.5
[16 empty] | 450.4976 |  | Loop 9 Maximum |  |  |  | 450 | [7 empty] | 2.5
[16 empty] | 450.4976 |  | Loop 10 Maximum |  |  |  | 450
[16 empty] | 450.4976 |  | Loop 11 Maximum |  |  |  | 450
[16 empty] | 450.4976 |  | Loop 12 Maximum |  |  |  | 450
3: Select Loop Devices |  | Loop 3: Actions required in this section >; Loop 8: *Loop Devices - Manually enter the required device totals per loop
[9 empty] | Note: | An Error message will appear in the loop totals if the number of devices has exceeded the maximum for that specific loop
Loop Devices: Addressable |  | Loop 1: Quantities | [16 empty] | Loop Devices: Addressable |  |  |  | Device Current |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities |  |  |  |  | Quantities
|  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12 | [18 empty] | Addressed | Max Alm LED | Quiescent | Alarm | Loop 1 |  |  |  |  | Loop 2 |  |  |  |  | Loop 3 |  |  |  |  | Loop 4 |  |  |  |  | Loop 5 |  |  |  |  | Loop 6 |  |  |  |  | Loop 7 |  |  |  |  | Loop 8 |  |  |  |  | Loop 9 |  |  |  |  | Loop 10 |  |  |  |  | Loop 11 |  |  |  |  | Loop 12
Part Number | Description | [28 empty] | Part Number | Description |  |  | IQ(mA) | IA (mA) | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals | Devices | Addresses | Quiescent | Alarm | Alarm totals
DETECTORS & CALL POINTS | [29 empty] | DETECTORS & CALL POINTS
VDOT-PY | Optical Detector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-PY | Optical Detector | 1 | 8 | 0.2 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-H2 | Heat Detector RoR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-H2 | Heat Detector RoR | 1 | 8 | 0.2 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-H2(H) | Fixed Heat Detector Fixed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-H2(H) | Fixed Heat Detector Fixed | 1 | 8 | 0.2 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-PYH | Opto-Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-PYH | Opto-Heat | 1 | 8 | 0.2 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-DPH | Dual Optical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-DPH | Dual Optical | 1 | 8 | 0.2 | 5 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-MiniIP | Call Point Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-MiniIP | Call Point Module | 1 | 8 | 1.7 | 7.2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[33 empty] | 8 | [6 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
LOOP INTERFACES |  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12
LOOP INTERFACES
VDOT-DIP-SCI | Dual Input Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-DIP-SCI | Dual Input Module | 1 | 8 | 3 | 16.9 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-DOP-SCI | Dual Output Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-DOP-SCI | Dual Output Module | 1 | 8 | 0.6 | 3.3 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-ZMU-SCI | Zone Monitor Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-ZMU-SCI | Zone Monitor Module | 1 | 8 | 2.6 | 35.9 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-SCM-SCI | Sounder Control Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-SCM-SCI | Sounder Control Module | 1 | 8 | 0.8 | 3.6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-DOP-AC240V-SCI | Dual Output Module (MAINS) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-DOP-AC240V-SCI | Dual Output Module (MAINS) | 1 | 8 | 0.6 | 3.3 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
VDOT-STB-SCI | Short Circuit Isolator Base | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | VDOT-STB-SCI | Short Circuit Isolator Base | 1 | 8 | 0.1 | 22 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[33 empty] | 8 | [6 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
REMOTE INDICATORS |  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12
REMOTE INDICATORS
MKII-RL/W | Fyreye MKII Conv remote LED - Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | MKII-RL/W | Fyreye MKII Conv remote LED - Wall | 0 | 8 | 0 | 2.6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
MKII-RL/C | Fyreye MKII Conv remote LED - Ceiling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | MKII-RL/C | Fyreye MKII Conv remote LED - Ceiling | 0 | 8 | 0 | 2.6 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[33 empty] | 8 | [6 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loop Totals |  | Loop 1: Address Quantities
|  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12
| Total Devices >>>> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Addresses >>>> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maximum Permissable Addresses >>>> | 254 | 254 | 254 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loop Status >>>> | bar: Address Quantities Loop 1 to Address Quantities Loop 12
Loop Totals |  | Address Quantities Loop 1: Quiescent Current (mA)
|  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12
| This System >>>> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [22 empty] | Loop 1 |  |  |  |  | Loop 2 |  |  |  |  | Loop 3 |  |  |  |  | Loop 4 |  |  |  |  | Loop 5 |  |  |  |  | Loop 6 |  |  |  |  | Loop 7 |  |  |  |  | Loop 8 |  |  |  |  | Loop 9 |  |  |  |  | Loop 9 |  |  |  |  | Loop 9 |  |  |  |  | Loop 9
| Maximum Permissable >>>> | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
Loop Status >>>> | bar: Quiescent Current (mA) Loop 1 to Quiescent Current (mA) Loop 12
Loop Totals |  | Quiescent Current (mA) Loop 1: Alarm Current (mA)
|  | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Loop 5 | Loop 6 | Loop 7 | Loop 8 | Loop 9 | Loop 10 | Loop 11 | Loop 12
| This System >>>> | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maximum Permissable >>>> | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
Loop Status >>>> | bar: Alarm Current (mA) Loop 1 to Alarm Current (mA) Loop 12
4: Battery Calculation
|  | Actions required in this section > |  |  |  |  | NONE
Battery Capacity
[19 empty] | Quiescent |  |  |  |  | Alarm |  |  |  |  | 0
|  | Alarm Current (mA) Loop 5: Current >>>> |  |  |  |  | Iq(mA) = | 113 |  |  |  | Ia(mA) = | 125
|  | Alarm Current (mA) Loop 5: Times >>>> |  |  |  |  | Standby Ts (Hrs) = | 24 |  |  |  | Alarm Ta (Hrs) = | 0.5
|  | Alarm Current (mA) Loop 5: Current Required >>>>; Alarm Current (mA) Loop 6: including derating factor and 80% discharge >>>> |  |  |  |  | Iqtotl (mAh) = | 2712 |  |  |  | Iatot (mAh) = | 125
|  | Alarm Current (mA) Loop 5: Total Current in mAh >>>> | [9 empty] | Ictot (mAh) = | 2837
|  | Alarm Current (mA) Loop 5: Total Current in Ah >>>> | [9 empty] | Ictot (Ah) = | 2.837
|  | Alarm Current (mA) Loop 5: Minimum Battery Capacity Required >>>> | [9 empty] | Ib (Ah) = | 3.5463
Note: | Velocity Control Panels will accomodate batteries from 2 x 12V 7Ah up to 2 x 12V 38Ah)
VL-MMP6 2 x 12v 12Ah, VL-MMP10 2 x 12v 38Ah & VL-MMP26 2 x 12v 38Ah
5: Site Details
|  | Actions required in this section > |  |  |  |  | Site Details - Optional **Enter (if required) the site details, project reference etc.
Site Name: |  | Alarm Current (mA) Loop 11: Date: |  |  |  |  | Surveyor:
Site Address:
Project Reference: |  | Alarm Current (mA) Loop 2: Specific Panel Reference:
(for Multi Panel Sites)
Technical Support
Contact your supplier for technical support on this product.
Velocity detection policy is one of continual improvement and the right to change a specification at any time without notice is reserved. Whilst every care has been taken to ensure that the contents of this document are correct at time of publication, Velocity Detection Ltd
shall be under no liability whatsoever in respect of such contents.
Due to the complexity and inherent importance of a life risk type system then training on this equipment is essential, and commissioning should only be carried out by competent persons.
We cannot guarantee the operation of any equipment unless all documented instructions are complied with, without variation. E&OE
Velocity Detection over Time
Detection House
72-78, Morfa Rd
Swansea
SA1 2EN
GLT Exports Ltd,
Detection House
72-78, Morfa Rd
Swansea
SA1 2EN
For further please contact on the telephone or email above.We reserve the right to update and improve our specification at any time and without notice. Whilst care is taken to ensure that document is correct at time of publication, we cannot take any liability whatsoever in respect of such contents. We cannot guarantee the operation of any equipment unless all documented instructions are complied with, without variation. E&OE. Training and independent proof of competence on this equipment is essential, and commissioning should only be carried out by those competent to do so.
Issue 0.001
For further info please contact on the telephone or email above.We reserve the right to update and improve our specification at any time and without notice. Whilst care is taken to ensure that document is correct at time of publication, we cannot take any liability whatsoever in respect of such contents. We cannot guarantee the operation of any equipment unless all documented instructions are complied with, without variation. E&OE. Training and independent proof of competence on this equipment is essential, and commissioning should only be carried out by those competent to do so.
Issue 1

## Sec 3 - Report
Addressable Systems Loop Calculation Spreadsheet
Site Details: | [12 empty] | Date: | 0
Site Name: | [9 empty] | Project Reference
0 | [9 empty] | 0
Site Address: | [9 empty] | Specific Panel Reference (if required for multi panel site)
0 | [9 empty] | 0
[10 empty] | Surveyor: |  | 0
Control Panel: Analogue Addressable
Part Number | Description | [12 empty] | Totals
VL-MMP 6/0 | MMP 6 no Zone LED
| Conventional Sounders (max 900mA): Enter expected current load per panel (mA) | [12 empty] | 0
| 24V Auxilary Power (max 450mA): Enter expected current load per panel (mA) | [12 empty] | 0
[13 empty] | Total Control Panel Quiescent Current (mA): | 113
[13 empty] | Total Control Panel Alarm Current (mA): | 125
Loop Devices: Addressable
Part Number | Description | Lp1 | Lp2 | Lp3 | Lp4 | Lp5 | Lp6 | Lp7 | Lp8 | Lp9 | Lp10 | Lp11 | Lp12 | Dev Total
DETECTORS & CALL POINTS
VDOT-PY | Optical Detector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-H2 | Heat Detector RoR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-H2(H) | Fixed Heat Detector Fixed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-PYH | Opto-Heat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-DPH | Dual Optical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-MiniIP | Call Point Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LOOP INTERFACES
VDOT-DIP-SCI | Dual Input Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-DOP-SCI | Dual Output Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-ZMU-SCI | Zone Monitor Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VDOT-SCM-SCI | Sounder Control Module | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
REMOTE INDICATORS
MKII-RL/W | Fyreye MKII Conv remote LED - Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MKII-RL/C | Fyreye MKII Conv remote LED - Ceiling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Loop Device Totals: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Loop Addr Totals: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Loop Max Addresses: | 254 | 254 | 254 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1016
| Loop Device Address Status: | [12 empty] | OK | bar: Lp1 to Lp12
| Quiescent Current Totals (mA): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Alarm Current Totals (mA): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selected Max Loop Current (mA): | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 5400
| Loop Load Current Status: | [12 empty] | OK | bar: Lp1 to Lp12
Battery Capacity |  | Lp3: Quiescent; Lp12: Alarm | Combined
| Loop & Panel Current (mA): | Lp2: Iq(mA); Lp3: 113; Lp5: IA(mA); Lp11: 125 | \/
| Standby & Alarm Times (Hrs): | Lp2: Ts (Hrs); Lp3: 24; Lp5: Ta (Hrs); Lp11: 0.5 | \/
| Current Required (mAH): | Lp2: Iqtot (mAh); Lp3: 2712; Lp5: Iatot (mAh); Lp11: 125 | \/
| Total Current (mAh): | Lp12: Ictot(mAh) | 2837
| Total Current (Ah): | Lp12: Ictot(Ah) | 2.837
| Minimum Battery Capacity Required (AH): | Lp12: Ib (Ah) | 3.5463
Velocity Detection
| Detection House, 72-78 Morfa Rd, | Lp2: E: technical@zetaalarmsystems.com
| Swansea UK. SA1 2EN | Lp2: T; =44 (0)1792 455 175
GLT Exports Ltd,
Detection House
72-78, Morfa Rd
Swansea
SA1 2EN
For further please contact on the telephone or email above.We reserve the right to update and improve our specification at any time and without notice. Whilst care is taken to ensure that document is correct at time of publication, we cannot take any liability whatsoever in respect of such contents. We cannot guarantee the operation of any equipment unless all documented instructions are complied with, without variation. E&OE. Training and independent proof of competence on this equipment is essential, and commissioning should only be carried out by those competent to do so.
Issue 0.001